MODELLING AND SIMULATION OF A WATER DISTRIBUTION NETWORK USING EPANET AND MATLAB

ABSTRACT

This assignment involved developing and analysing a water distribution network using EPANET and MATLAB. The EPANET MATLAB Toolkit was installed and configured to enable communication between MATLAB and the EPANET hydraulic simulation engine. A network input file was loaded into MATLAB, and several toolkit functions were tested to retrieve information about nodes, links, elevations, pipe lengths, diameters, roughness coefficients, and flow units. The network consisted of four nodes, comprising two junctions, one reservoir, and one tank, connected by three pipes. Hydraulic simulation results were retrieved for node hydraulic heads and pressures, as well as pipe flows, velocities, and head losses. MATLAB was also used to display the network layout and organise simulation results into tables and CSV files. The exercise demonstrated how MATLAB can be used to inspect, simulate, and analyse a water distribution network through the EPANET Toolkit.

CHAPTER ONE: INTRODUCTION

1.1 Background

Water distribution networks consist of interconnected pipes, reservoirs, tanks, pumps, valves, and demand points. Hydraulic analysis is important in understanding how water flows through such systems and determining the pressure and flow conditions at different locations.

EPANET is a software application developed for modelling water distribution systems. It can calculate hydraulic conditions throughout a network based on its physical characteristics, demands, and operating settings.

MATLAB is a numerical computing environment that supports data processing, calculations, plotting, and automation. The EPANET MATLAB Toolkit allows MATLAB users to access EPANET functions and retrieve network and simulation information programmatically.

1.2 Aim

To model and simulate a water distribution network using EPANET and MATLAB and investigate the functions available in the EPANET MATLAB Toolkit.

1.3 Objectives

The objectives were to:

- Install and configure the EPANET MATLAB Toolkit.

- Load a water distribution network input file into MATLAB.

- identify and inspect network nodes and links.

- Test functions for retrieving network properties.

- Plot the network layout using MATLAB.

- Execute hydraulic simulation and retrieve computed results.

- Present the results in tables and CSV files.

1.4 Scope

The work focused on a small network containing four nodes and three pipes. It included network inspection, visualisation, toolkit function testing, hydraulic simulation, and presentation of results. The analysis was based on the supplied network model and its input settings.

CHAPTER TWO: SOFTWARE AND METHODOLOGY

2.1 Software Used

The following software and files were used:

- EPANET: for modelling and analysing the water distribution network.

- MATLAB: for loading the network, calling toolkit functions, plotting, and processing results.

- EPANET MATLAB Toolkit: for communication between MATLAB and the EPANET simulation engine.

- Network input file: my_network.inp.

- MATLAB scripts: for inspecting and simulating the network.

- CSV files: for storing node and link simulation results.

2.2 Loading the Network

The network was loaded into MATLAB using the following command:

d = epanet('my_network.inp');

This created an EPANET object named d, through which network properties and simulation functions could be accessed.

The number of nodes and links was checked using:

d.getNodeCount

d.getLinkCount

The output indicated four nodes and three links.

2.3 Inspection of Network Properties

The following functions were tested:

d.getNodeNameID

d.getNodeElevations

d.getNodeType

d.getNodeBaseDemands

d.getLinkNameID

d.getLinkLength

d.getLinkDiameter

d.getLinkRoughnessCoeff

d.getFlowUnits

d.getConnectivityMatrix

These functions were used to inspect node identities, elevations, node types, base demands, pipe properties, flow units, and network connectivity.

2.4 Network Visualisation

The network was plotted using:

figure;

d.plot;

The plot provided a visual representation of the network arrangement and its connections.

2.5 Hydraulic Simulation

The complete simulation command was executed using:

d.runsCompleteSimulation;

The toolkit completed this command without reporting an error in the recorded MATLAB session. Hydraulic results were then retrieved using functions for node hydraulic head, node pressure, link flow, link velocity, and link head loss.

The results were organised into MATLAB tables and exported to CSV files for storage and further analysis.

CHAPTER THREE: NETWORK DESCRIPTION

3.1 Network Components

The model consisted of the following components:

| Component | Quantity | Identification |
| --- | --- | --- |
| Junctions | 2 | J1 and J2 |
| Reservoirs | 1 | R1 |
| Tanks | 1 | T1 |
| Pipes | 3 | P1, P2 and P3 |
| Total nodes | 4 | J1, J2, R1 and T1 |
| Total links | 3 | P1, P2 and P3 |

3.2 Node Properties

The node elevations retrieved from MATLAB are shown below.

| Node | Node type | Elevation (m) |
| --- | --- | --- |
| J1 | Junction | 100 |
| J2 | Junction | 95 |
| R1 | Reservoir | 130 |
| T1 | Tank | 90 |

The base demands returned by MATLAB were 0.5 L/s at J1 and 0.3 L/s at J2, with zero base demand reported for the reservoir and tank entries.

3.3 Pipe Properties

| Pipe | Length (m) | Diameter (mm) | Roughness coefficient |
| --- | --- | --- | --- |
| P1 | 1000 | 200 | 130 |
| P2 | 800 | 150 | 130 |
| P3 | 500 | 150 | 130 |

The network used litres per second (L/s) as its flow units. The pipe roughness coefficients were reported as 130 for all three pipes.

CHAPTER FOUR: RESULTS AND DISCUSSION

4.1 Node Hydraulic Results

The MATLAB simulation returned the following node results.

| Node | Elevation (m) | Hydraulic head (m) | Pressure head (m) |
| --- | --- | --- | --- |
| J1 | 100 | 124.26 | 24.257 |
| J2 | 95 | 106.13 | 11.132 |
| R1 | 130 | 130.00 | Approximately 0 |
| T1 | 90 | 95.00 | 5.00 |

Source: MATLAB output obtained from the network simulation.

Hydraulic head represents the total hydraulic energy per unit weight of water, expressed as a height. Pressure head represents the pressure expressed as an equivalent height of water.

J1 had a reported pressure head of 24.257 m, while J2 had 11.132 m. This indicates that the computed pressure head at J1 was higher than that at J2 under the modelled conditions. The tank pressure head was reported as 5 m. The reservoir pressure result was approximately zero, which is consistent with the reservoir's specified hydraulic head.

4.2 Pipe Hydraulic Results

| Pipe | Flow (L/s) | Velocity (m/s) | Head loss (m) |
| --- | --- | --- | --- |
| P1 | 32.396 | 1.0312 | 5.7429 |
| P2 | 31.896 | 1.8050 | 18.125 |
| P3 | 31.596 | 1.7880 | 11.132 |

Source: MATLAB output obtained from the network simulation.

Flow rate represents the volume of water passing through a pipe per unit time. Velocity represents the speed of water inside the pipe. Head loss represents the reduction in hydraulic head associated with flow through the pipe under the modelled conditions.

P1 had the lowest reported velocity, at 1.0312 m/s, and the lowest head loss, at 5.7429 m. P2 had the highest reported head loss, at 18.125 m. Its smaller diameter compared with P1 is one factor that may influence hydraulic resistance, although the effect also depends on flow rate, pipe length, and the selected head-loss model.

The reported flows were 32.396 L/s in P1, 31.896 L/s in P2, and 31.596 L/s in P3. These values should be interpreted alongside the network's connection arrangement, tank behaviour, and simulation settings. They should not be assumed to represent a validated real installation without further checks.

4.3 Testing of Toolkit Functions

Several functions were tested during the assignment.

| Function | Purpose |
| --- | --- |
| getNodeCount | Returns the number of nodes |
| getLinkCount | Returns the number of links |
| getNodeNameID | Retrieves node identification labels |
| getNodeElevations | Retrieves node elevations |
| getNodeType | Identifies node types |
| getNodeBaseDemands | Retrieves base demand values |
| getLinkNameID | Retrieves link identification labels |
| getLinkLength | Retrieves pipe lengths |
| getLinkDiameter | Retrieves pipe diameters |
| getLinkRoughnessCoeff | Retrieves pipe roughness coefficients |
| getFlowUnits | Identifies the network's flow units |
| getConnectivityMatrix | Represents connections between network nodes |
| plot | Displays the network layout |
| runsCompleteSimulation | Executes the complete simulation workflow |
| getNodeHydraulicHead | Retrieves computed node hydraulic heads |
| getNodePressure | Retrieves computed node pressures |
| getLinkFlows | Retrieves computed link flow rates |
| getLinkVelocity | Retrieves computed link velocities |
| getLinkHeadloss | Retrieves computed link head losses |

The function tests demonstrated that MATLAB could access the network's structural information and retrieve computed hydraulic results. The results were also organised into tables and exported as CSV files.

4.4 Saving Results

The node and link results were exported to:

- drawn_node_results.csv

- drawn_link_results.csv

These files can be opened in spreadsheet software for further analysis or included as supporting material in the assignment.

4.5 Limitations

The model represents a small example network rather than a verified real water distribution system. The results depend on the input file's elevations, demands, pipe dimensions, roughness coefficients, reservoir head, tank settings, and simulation options.

The input model's simulation duration should be checked before interpreting the results as extended-period behaviour. A single-period hydraulic analysis does not demonstrate how tank levels, pressures, and flows change over a full day. The model should also be checked in EPANET desktop to confirm that it runs successfully and that its reported results agree with those obtained through MATLAB.

CHAPTER FIVE: CONCLUSION AND RECOMMENDATIONS

5.1 Conclusion

The assignment demonstrated how EPANET can be used together with MATLAB to inspect and simulate a water distribution network. The network input file was loaded successfully, and the toolkit returned four nodes and three links. Functions for retrieving node information, pipe properties, flow units, and connectivity were tested. The network was plotted, and hydraulic results for node heads and pressures and pipe flows, velocities, and head losses were retrieved and organised into tables and CSV files.

The work provided practical experience in using MATLAB to interact with EPANET and process water distribution network data. It also showed the importance of checking simulation settings and validating computed results before drawing engineering conclusions.

5.2 Recommendations

- Verify the network input file and simulation results using EPANET desktop.

- Check the simulation duration and run an extended-period analysis if required by the assignment.

- Examine tank settings and operating conditions to ensure that the model represents the intended system.

- Preserve the MATLAB scripts, input file, output tables, and network diagram for reproducibility.

- For future work, investigate how changing pipe diameters, demands, reservoir head, and tank settings affects network performance.

REFERENCES

- U.S. Environmental Protection Agency (EPA). EPANET: Application for Modeling Drinking Water Distribution Systems. https://www.epa.gov/water-research/epanet

- OpenWaterAnalytics. EPANET Source Code and Project Resources. https://github.com/OpenWaterAnalytics/EPANET

- OpenWaterAnalytics. EPANET MATLAB Toolkit. Toolkit documentation and source files used for the MATLAB interface.

APPENDICES

Appendix A: MATLAB scripts used for network creation, inspection, and simulation.

Appendix B: my_network.inp network input file.

Appendix C: drawn_node_results.csv and drawn_link_results.csv.

Appendix D: Screenshot of the MATLAB network plot and simulation output.